## Code Information
Column_1	Column_2	Column_3	Column_4
Applicable Codes:	General: / • Building/Dwelling Code IBC 2015 / • (WI Commercial Building Code SPS 362) / Existing: / • International Existing Building Code 2015 / • (WI Commercial Building Code SPS 366) / Energy Conservation: / • International Energy Conservation Code 2015 / • (WI Commercial Building Code v363) / Plumbing: / • WI Commercial Building Code SPS 381-387 / Mechanical: / • Mechanical Code IMC 2015 / • (WI Commercial Building Code SPS 364) / Electrical: / • Electrical Code NEC 2008 / • (WI Commercial Building Code SPS 316 / Fire: / • Fire/Life Safety Code 2009 NFPA-1 / • (WI Commercial Building Code SPS 314 & 330) / Accessibility: / • ANSI Standard A117.1-2009- for Accessibility / • (WI Commercial Building Code SPS 362) / Fuel: / • International Fuel Gas Code 2009 / • (WI Commercial Building Code Chapter 365)
Sprinklers (Section 903 Automatic Sprinkler Systems):	No	https://up.codes/viewer/wyoming/ibc-2015/chapter/9/fire-protection-systems#903
Basement:	No Basement
Chapter 5 Classification of Work:	New	https://up.codes/viewer/wyoming/iebc-2015/chapter/5/classification-of-work#5
Chapter 3 Use and Occupancy Classification:	311.2 Moderate-Hazard Storage, Group S-1	https://up.codes/viewer/wyoming/ibc-2015/chapter/3/use-and-occupancy-classification#3	- Assembly (see Section 303): Groups A-1, A-2, A-3, A-4 and A-5. / - Business (see Section 304): Group B. / - Educational (see Section 305): Group E. / - Factory and Industrial (see Section 306): Groups F-1 and F-2. / - High Hazard (see Section 307): Groups H-1, H-2, H-3, H-4 and H-5. / - Institutional (see Section 308): Groups I-1, I-2, I-3 and I-4. / - Mercantile (see Section 309): Group M. / - Residential (see Section 310): Groups R-1, R-2, R-3 and R-4. / - Storage (see Section 311): Groups S-1 and S-2. / - Utility and Miscellaneous (see Section 312): Group U.
Chapter 4 Special Detailed Requirements Based on Use and Occupancy:	406.8 Repair Garages
Section 602 Construction Classification:	VB	https://up.codes/viewer/wyoming/ibc-2015/chapter/6/types-of-construction#602
Table 504.3a Allowable Building Height In Feet Above Grade Plane:	Allowed:1 / Actual:1	https://up.codes/viewer/wyoming/ibc-2015/chapter/5/general-building-heights-and-areas#504.3
506.2 Allowable Area Determination:	9000 sf	https://up.codes/viewer/wyoming/ibc-2015/chapter/5/general-building-heights-and-areas#506.2
506.3 Frontage Increase:	Calculation not used	https://up.codes/viewer/wyoming/ibc-2015/chapter/5/general-building-heights-and-areas#506.3
508.3 Nonseparated Occupancies:	N/A	https://up.codes/viewer/wyoming/ibc-2015/chapter/5/general-building-heights-and-areas#508.3
508.4 Separated Occupancies	N/A	https://up.codes/viewer/wyoming/ibc-2015/chapter/5/general-building-heights-and-areas#508.4
Table 602 Fire-resistance Rating Requirements For Exterior Walls Based On Fire Separation Distance:	Structural Frame: 0 hr / Bearing Walls- exterior: 0 hr / Bearing Walls-interior: 0 hr / Non-bearing walls-exterior - / Fire Separation Distance / • X < 5c = 0 hr / • 5 = X< 10 = 0 hr / • 10 = X< 30 = 0 hr / • X = 30 = 0 hr / Non-bearing walls-interior: 0 hr / Floor Construction: 0 hr / Roof Construction: 0 hr	https://up.codes/viewer/wyoming/ibc-2015/chapter/6/types-of-construction#602
Table 1020.1 Corridor Fire-resistance Rating:	0 hr with Sprinklers	https://up.codes/viewer/wyoming/ibc-2015/chapter/10/means-of-egress#1020
1006.2.1 Egress Based on Occupant Load and Common Path of Egress Travel Distance:	Maximum Common Path without Sprinkler System: 75ft / Maximum Occupant Load Of Space With One Exit: / • M: 49ft	https://up.codes/viewer/wyoming/ibc-2015/chapter/10/means-of-egress#1006.2.1
Section 1017 Exit Access Travel Distance:	Maximum Exit Access Travel Distance without Sprinklers: 200ft	https://up.codes/viewer/wyoming/ibc-2015/chapter/10/means-of-egress#1017
1020.4 Dead Ends:	20ft	https://up.codes/viewer/wyoming/iebc-2015/chapter/8/alterations-level-2#805.6	https://up.codes/viewer/wyoming/ibc-2015/chapter/10/means-of-egress#1020.4
Table 906.3(1) Fire Extinguishers For Class A Fire Hazards	Type 2-A: / • (everywhere except kitchen) / • Maximum Floor Area Per Unit of A: 1,500sf / • Maximum Distance to Extinguisher: 75ft / • Hazard Classification: Ordinary (Moderate)	https://up.codes/viewer/wyoming/ifc-2015/chapter/9/fire-protection-systems#906
2902.1 Minimum Number of Fixtures	Classification & Occupancy: / • S1 / Water Closets: 1 per100 / • Women (Required/Provided) 1/1 / • Men (Required/Provided): 1/1 / Lavatories: 1 per 100 / • Women (Required/Provided) 1/1 / • Men (Required/Provided): 1/1	https://up.codes/viewer/wyoming/ibc-2015/chapter/29/plumbing-systems#2902.1

	Type K: / • 2.5-gallon or (2)1.5-gallon / • Maximum Distance to Extinguisher:Within 30ft of cooking equipment / • Hazard Classification:Ordinary (Moderate)

	Bathtubs/Showers: N/A / Drinking Fountains: / • (Required/Provided): 1/1 / Other: N/A

## 506.2
CLASSIFICATION		TYPE I		TYPE II		TYPE III		TYPE IV	TYPE V
		A	B	A	B	A	B	HT	A	B
A-1	NS	UL	UL	15,500	8,500	14,000	8,500	15,000	11,500	5,500
U	NS	UL	35,500	19,000	8,500	14,000	8,500	18,000	9,000	5,500
A-2	NS	UL	UL	15,500	9,500	14,000	9,500	15,000	11,500	6,000
A-3	NS	UL	UL	15,500	9,500	14,000	9,500	15,000	11,500	6,000
A-4	NS	UL	UL	15,500	9,500	14,000	9,500	15,000	11,500	6,000
F-1	NS	UL	UL	25,000	15,500	19,000	12,000	33,500	14,000	8,500
B	NS	UL	UL	37,500	23,000	28,500	19,000	36,000	18,000	9,000
M	NS	UL	UL	21,500	12,500	18,500	12,500	20,500	14,000	9,000
S-1	NS	UL	48,000	26,000	17,500	26,000	17,500	25,500	14,000	9,000
E	NS	UL	UL	26,500	14,500	23,500	14,500	25,500	18,500	9,500
F-2	NS	UL	UL	37,500	23,000	28,500	18,000	50,500	21,000	13,000
S-2	NS	UL	79,000	39,000	26,000	39,000	26,000	38,500	21,000	13,500
A-5	NS	UL	UL	UL	UL	UL	UL	UL	UL
H-2	NSc	21,000	16,500	11,000	7,000	9.5	7,000	10,500	7,500	3,000
H-3	NSc	UL	60,000	26,500	14,000	17,500	13,000	25,500	10,000	5,000
H-1	NSc	21,000	16,500	11,000	7,000	9.5	7,000	10,500	7,500	NP
H-4	NSc, d	UL	UL	37,500	17,500	28,500	17,500	36,000	18,000	6,500
H-5	NSc, d	UL	UL	37,500	23,000	28,500	19,000	36,000	18,000	9,000
I-1	NSd, e	UL	55,000	19,000	10,000	16,500	10,000	18,000	10,500	4,500
I-3	NSd, e	UL	UL	15,000	10,000	10,500	7,500	12,000	7,500	5,000
I-2	NSd, f	UL	UL	15,000	11,000	12,000	NP	12,000	9,500	NP
I-4	NSd, g	UL	60.5	26,500	13,000	23,500	13,000	25,500	18,500	9,000
R-1	NSd, h	UL	UL	24,000	16,000	24,000	16,000	20,500	12,000	7,000
R-2	NSd, h	UL	UL	24,000	16,000	24,000	16,000	20,500	12,000	7,000
R-4	NSd, h	UL	UL	24,000	16,000	24,000	16,000	20,500	12,000	7,000
R-3	NSd, h	UL	UL	UL	UL	UL	UL	UL	UL
H-2	S1	21,000	16,500	11,000	7,000	9.5	7,000	10,500	7,500	3,000
H-3	S1	UL	60,000	26,500	14,000	17,500	13,000	25,500	10,000	5,000
I-1	S1	UL	220,000	76,000	40,000	66,000	40,000	72,000	42,000	18,000
I-3	S1	UL	UL	45,000	40,000	42,000	30,000	48,000	30,000	20,000
A-1	S1	UL	UL	62,000	34,000	56,000	34,000	60,000	46,000	22,000
U	S1	UL	142,000	76,000	34,000	56,000	34,000	72,000	36,000	22,000
A-2	S1	UL	UL	62,000	38,000	56,000	38,000	60,000	46,000	24,000
A-3	S1	UL	UL	62,000	38,000	56,000	38,000	60,000	46,000	24,000
A-4	S1	UL	UL	62,000	38,000	56,000	38,000	60,000	46,000	24,000
H-4	S1	UL	UL	150,000	70,000	114,000	70,000	144,000	72,000	26,000
R-1	S1	UL	UL	96,000	64,000	96,000	64,000	82,000	48,000	28,000
R-2	S1	UL	UL	96,000	64,000	96,000	64,000	82,000	48,000	28,000
R-4	S1	UL	UL	96,000	64,000	96,000	64,000	82,000	48,000	28,000
F-1	S1	UL	UL	100,000	62,000	76,000	48,000	134,000	56,000	34,000
B	S1	UL	UL	150,000	92,000	114,000	76,000	144,000	72,000	36,000
H-5	S1	UL	UL	150,000	92,000	114,000	76,000	144,000	72,000	36,000
I-4	S1	UL	121,000	106,000	52,000	94,000	52,000	102,000	74,000	36,000
M	S1	UL	UL	86,000	50,000	74,000	50,000	82,000	56,000	36,000
S-1	S1	UL	192,000	104,000	70,000	104,000	70,000	102,000	56,000	36,000
E	S1	UL	UL	106,000	58,000	94,000	58,000	102,000	74,000	38,000
F-2	S1	UL	UL	150,000	92,000	114,000	72,000	202,000	84,000	52,000
S-2	S1	UL	316,000	156,000	104,000	156,000	104,000	154,000	84,000	54,000
H-1	S1	21,000	16,500	11,000	7,000	9.5	7,000	10,500	7,500	NP
I-2	S1	UL	UL	60,000	44,000	48,000	NP	48,000	38,000	NP
A-5	S1	UL	UL	UL	UL	UL	UL	UL	UL
R-3	S1	UL	UL	UL	UL	UL	UL	UL	UL
R-1	S13R	UL	UL	24,000	16,000	24,000	16,000	20,500	12,000	7,000
R-2	S13R	UL	UL	24,000	16,000	24,000	16,000	20,500	12,000	7,000
R-4	S13R	UL	UL	24,000	16,000	24,000	16,000	20,500	12,000	7,000
R-3	S13R	UL	UL	UL	UL	UL	UL	UL	UL
H-2	SM	21,000	16,500	11,000	7,000	9.5	7,000	10,500	7,500	3,000
H-3	SM	UL	60,000	26,500	14,000	17,500	13,000	25,500	10,000	5,000
I-1	SM	UL	165,000	57,000	30,000	49,500	30,000	54,000	31,500	13,500
I-3	SM	UL	UL	45,000	30,000	31,500	22,500	36,000	22,500	15,000
A-1	SM	UL	UL	46,500	25,500	42,000	25,500	45,000	34,500	16,500
U	SM	UL	106,500	57,000	25,500	42,000	25,500	54,000	27,000	16,500
A-2	SM	UL	UL	46,500	28,500	42,000	28,500	45,000	34,500	18,000
A-3	SM	UL	UL	46,500	28,500	42,000	28,500	45,000	34,500	18,000
A-4	SM	UL	UL	46,500	28,500	42,000	28,500	45,000	34,500	18,000
H-4	SM	UL	UL	112,500	52,500	85,500	52,500	108,000	54,000	19,500
R-1	SM	UL	UL	72,000	48,000	72,000	48,000	61,500	36,000	21,000
R-2	SM	UL	UL	72,000	48,000	72,000	48,000	61,500	36,000	21,000
R-4	SM	UL	UL	72,000	48,000	72,000	48,000	61,500	36,000	21,000
F-1	SM	UL	UL	75,000	46,500	57,000	36,000	100,500	42,000	25,500
B	SM	UL	UL	112,500	69,000	85,500	57,000	108,000	54,000	27,000
H-5	SM	UL	UL	112,500	69,000	85,500	57,000	108000	54,000	27,000
I-4	SM	UL	181,500	79,500	39,000	70,500	39,000	76,500	55,500	27,000
M	SM	UL	UL	64,500	37,500	55,500	37,500	61,500	42,000	27,000
S-1	SM	UL	144,000	78,000	52,500	78,000	52,500	76,500	42,000	27,000
E	SM	UL	UL	79,500	43,500	70,500	43,500	76,500	55,500	28,500
F-2	SM	UL	UL	112,500	69,000	85,500	54,000	151,500	63,000	39,000
S-2	SM	UL	237,000	117,000	78,000	117,000	78,000	115,500	63,000	40,500
I-2	SM	UL	UL	45,000	33,000	36,000	NP	36,000	28,500	NP
A-5	SM	UL	UL	UL	UL	UL	UL	UL	UL
R-3	SM	UL	UL	UL	UL	UL	UL	UL	UL

## 1006.2.1
OCCUPANCY	MAXIMUM OCCUPANT	MAXIMUM COMMON PATH OF EGRESS TRAVEL DISTANCE (feet)
	LOAD OF SPACE	Without Sprinkler System		With Sprinkler System
		(feet)		(feet)
		Occupant Load
		OL ≤ 30	OL > 30
Ac, E, M	49	75	75	75a
B	49	100	75	100a
F	49	75	75	100a
H-1, H-2, H-3	3	NP	NP	25b
H-4, H-5	10	NP	NP	75b
I-1, I-2d, I-4	10	NP	NP	75a
I-3	10	NP	NP	100a
R-1	10	NP	NP	75a
R-2	10	NP	NP	125a
R-3e	10	NP	NP	125a
R-4e	10	75	75	125a
Sf	29	100	75	100a
U	49	100	75	75a

## 1017.2
OCCUPANCY	WITHOUT SPRINKLER	WITH SPRINKLER
	SYSTEM	SYSTEM
	(feet)	(feet)
A, E, F-1, M, R, S-1	200	250b
I-1	Not Permitted	250b
B	200	300c
F-2, S-2, U	300	400c
H-1	Not Permitted	75d
H-2	Not Permitted	100d
H-3	Not Permitted	150d
H-4	Not Permitted	175d
H-5	Not Permitted	200c
I-2, I-3, I-4	Not Permitted	200c

## Save
	Building perimeter lengths (ft)	Distance to property line or to far side of R.O.W. (ft)
facing north:	431	60+
facing east:	250	60+
facing south:	431	60+
facing west:	123	17
	79	41
	49	60+

Allowable Areas and Heights / Type IIIB / Factory (F-2) Occupancy
	Allowable area per floor:	41249 sq.ft.
	Total allowable area:	41249 sq.ft.
	Maximum allowable height:	55 ft.
	Maximum allowable stories:	3

Allowable Areas and Heights / Type IIIB / Business (B) Occupancy	Allowable area per floor:	31523 sq.ft.
	Total allowable area:	31523 sq.ft.
	Maximum allowable height:	55 ft.
	Maximum allowable stories:	3