## Code Information
Column_1	Column_2	Column_3	Column_4
Applicable Codes:
	General:	Building/Dwelling Code IBC 2009 (WI Commercial Building Code SPS 362)
	Existing:	International Existing Building Code 2009 (WI Commercial Building Code SPS 366)
	Energy Conservation:	International Energy Conservation Code 2009 (WI Commercial Building Code v363)
	Plumbing:	International Plumbing Code (WI Commercial Building Code SPS 381-387)
	Mechanical:	Mechanical Code IMC 2009 (WI Commercial Building Code SPS 364)
	Electrical	Electrical Code NEC 2008(WI Commercial Building Code SPS 316
	Fire:	Fire/Life Safety Code 2009 NFPA-1 (WI Commercial Building Code SPS 314 & 330)
	Accessibility:	ANSI Standard A117.1-2009- for Accessibility (WI Commercial Building Code SPS 362)
	Fuel:	International Fuel Gas Code 2009 (WI Commercial Building Code Chapter 365)
Sprinklers:	No		https://up.codes/viewer/alabama/int_building_code_2009/chapter/9/fire-protection-systems#903
Basement:	No Basement
Alteration Level (IEBC 405):	Level 2		https://up.codes/viewer/pennsylvania/int_ebc_2009/chapter/4/classification-of-work#404
Occupancy Types (302.1):	Factory Industrial F-2 Low-Hazard Occupancy		https://up.codes/viewer/alabama/int_building_code_2009/chapter/3/use-and-occupancy-classification#302
	Business Group B
Type of Construction:	TYPE III-B		https://up.codes/viewer/alabama/int_building_code_2009/chapter/6/types-of-construction#602
Number of Stories	1 Story (w/ Mezzanine)
SECTION 506 BUILDING AREA MODIFICATIONS			https://up.codes/viewer/alabama/int_building_code_2009/chapter/5/general-building-heights-and-areas#506
	Building perimeter lengths (ft)	Distance to property line or to far side of R.O.W. (ft)
facing north:	431	60+
facing east:	250	60+
facing south:	431	60+
facing west:	123	17
	79	41
	49	60+

Allowable Areas and Heights / Type IIIB / Factory (F-2) Occupancy
	Allowable area per floor:	41249 sq.ft.
	Total allowable area:	41249 sq.ft.
	Maximum allowable height:	55 ft.
	Maximum allowable stories:	3

Allowable Areas and Heights / Type IIIB / Business (B) Occupancy	Allowable area per floor:	31523 sq.ft.
	Total allowable area:	31523 sq.ft.
	Maximum allowable height:	55 ft.
	Maximum allowable stories:	3
TABLE 601- FIRE-RESISTANCE RATING REQUIREMENTS FOR BUILDING ELEMENTS (hours)	Structural Frame:	0 hr	https://up.codes/viewer/alabama/int_building_code_2009/chapter/6/types-of-construction#602.1
	Bearing Walls- exterior:	2 hr
	Bearing Walls-interior:	0 hr
	Non-bearing walls-exterior - / Fire Separation Distance
		X < 5c = 1 hr
		5 = X< 10 = 1 hr
		10 = X< 30 = 1 hr
		X = 30 = 0 hr
	Non-bearing walls-interior:	0 hr
	Floor Construction:	0 hr
	Roof Construction:	0 hr

Corridor Fire Resistance Rating (Table 1018.1)	1 hr without Sprinklers		https://up.codes/viewer/alabama/int_building_code_2009/chapter/10/means-of-egress#1018
Common Path of Egress Travel: (1014.3)	75		https://up.codes/viewer/alabama/int_building_code_2009/chapter/10/means-of-egress#1014.3
Maximum Travel Distance: (1016.1)	B: 200ft		https://up.codes/viewer/alabama/int_building_code_2009/chapter/10/means-of-egress#1016
	F-2: 300ft
Min. number of exits less than 500 (Table 1015.1 & Table 1021.1)	2		https://up.codes/viewer/alabama/int_building_code_2009/chapter/10/means-of-egress#1015
Dead end corridor max. length	Existing (IEBC 805.6): 35ft		https://up.codes/viewer/wyoming/iebc-2015/chapter/8/alterations-level-2#805.6
	New Construction (1018.4): 20ft		https://up.codes/viewer/alabama/ibc-2009/chapter/10/means-of-egress#1018.4
Fire Extinguishers:	Type 2-A: (everywhere except kitchen)		https://up.codes/viewer/alabama/ibc-2009/chapter/9/fire-protection-systems#906.3
	Maximum Floor Area Per Unit of A:	1,500sf
	Maximum Distance to Extinguisher:	75ft
	Hazard Classification:	Ordinary (Moderate)

	Type K:
	2.5-gallon or (2)1.5-gallon
	Maximum Distance to Extinguisher:	Within 30ft of cooking equipment
	Hazard Classification:	Ordinary (Moderate)